## cDAQ data points & wiring notes
| DAQ modules and wiring notes |  |  |  | updated 12/31/25
MH DAQ MAP
CHASSIS | MODULE | CHANNEL | SENSOR | VOLTAGE | VARIABLE | NOTES | WIRING NOTES | signal | common | excitation (-) | excitation (+)
cDAQ-9178 | 1: NI 9201 AI module NOTE all Setras currently disconnected | 0 | Setra 264 | 0-5 V | dP_Liv-Hi_M1_C0 | n/a | brown = signal, white = common [excitation at Setra: black = (-); red = (+) at 12VDC wall wart] | brown | white | black at wall wart 12VDC | red at wall wart 12VDC
|  | 1 | Setra 264 | 0-5 V | dP_Liv-Lo_M1_C1 | n/a | red = signal, black = common [excitation at Setra: black = (-); red = (+) at 12VDC wall wart] | red | black | black at wall wart 12VDC | red at wall wart 12VDC
|  | 2 | Setra 264 | 0-5 V | dP_Bed3-E-Hi_M1_C2 | n/a | blue = signal (jumpers to red extension wire at Setra); clear/white = common (jumpers to black extension wire at Setra) [excitation at Setra: black = (-); red = (+) at 12VDC wall wart] | red to blue | clear/white to black | black at wall wart 12VDC | red at wall wart 12VDC
|  | 3 | Setra 264 | 0-5 V | dP_Bed3-E-Lo_M1_C3 | n/a | red = signal, black = common [excitation at Setra: black = (-); red = (+) at 12VDC wall wart] | red | black | black at wall wart 12VDC | red at wall wart 12VDC
|  | 4 | Setra 264 | 0-5 V | dP_Fam-S-Hi_M1_C4 | n/a | blue = signal; clear/white = common [excitation at Setra: black = (-); red = (+) at 12VDC wall wart] | blue | clear/white | black at wall wart 12VDC | red at wall wart 12VDC
|  | 5 | Setra 264 | 0-5 V | dP_Fam-S-Lo_M1_C5 | n/a | blue = signal; clear/white = common [excitation at Setra: black = (-); red = (+) at 12VDC wall wart] | blue | clear/white | black at wall wart 12VDC | red at wall wart 12VDC
|  | 6 | Setra 264 | 0-5 V | dP_Fam-W-Hi_M1_C6 | n/a | blue = signal; clear/white = common [excitation at Setra: black = (-); red = (+) at 12VDC wall wart] | blue | clear/white | black at wall wart 12VDC | red at wall wart 12VDC
|  | 7 | Setra 264 | 0-5 V | dP_Fam-W-Lo_M1_C7 | n/a | red = signal, black = common [excitation at Setra: black = (-); red = (+) at 12VDC wall wart] | red | black | black at wall wart 12VDC | red at wall wart 12VDC
| 2: NI 9201 AI module NOTE all Setras currently disconnected | 0 | Setra 264 | 0-5 V | dP_Attic_M2_C0 | n/a | white = signal, black = common, red = excitation +24VDC from DAQ power supply; green = (-) at DAQ power supply | white | black | green from (-) at VDC at DAQ power supply | red from (+) 24VDC at DAQ power supply
|  | 1 | Setra 264 | 0-5 V | dP_Crawl-E_M2_C1 | n/a | white = signal, black = common, red = excitation +24VDC from DAQ power supply; green = (-) at DAQ power supply | white | black | green from (-) at VDC at DAQ power supply | red from (+) 24VDC at DAQ power supply
|  | 2 | Setra 264 | 0-5 V | dP_Crawl-W_M2_C2 | n/a | white = signal, black = common, red = excitation +24VDC from DAQ power supply; green = (-) at DAQ power supply | white | black | green from (-) at VDC at DAQ power supply | red from (+) 24VDC at DAQ power supply
3
4
5
6
|  | 7 | 6VDC lantern batt | 6 V | 6V_Test_M2_C7 | constant voltage source = DAQ test channel | 6 VDC lantern battery housed in gray plastic 6"x6" junction box to right of DAQ rack; two leads connect to module and modules' common bus | white | black
| 3: NI 9201 AI module | 0 | Vaisala HMP155 | 0-10 VDC | RH_Bed1_M3_C0 | n/a | [Vaisala HMP155 s/n V1940954 calib 5/11/23] Vaisala white to wire black = temp signal at M4C4); Vaisala green to wire red = common, Vaisala yellow to wire brown = RH signal (M3C0), Vaisala blue to wire green = +24VDC at DAQ power supply, Vaisala red to wire white = (-) DCV at DAQ power supply (Vaisala brown, pink, black, gray taped aside with no connections) | Vyellow to IAQbrown | Vgreen to IAQred | Vred to IAQwhite at (-) VDC at DAQ power supply | Vblue to IAQgreen at (+) 24VDC at DAQ power supply | (Vaisala brown, pink, black, gray taped aside with no connections) | Vaisala white to wire black = temp signal at M4C4)
|  | 1 | Vaisala HMP45A | 0-1 VDC | RH_Bed2_M3_C1 | *Eventually replace with HMP155s | Vaisala yellow to wire black = temp signal at M4C5, Vaisala blue to wire green = +24VDC at DAQ power supply, Vaisala brown to wire brown = RH signal at M3C1, Vaisala purple and Vaisala red to wire red = common and wire white = (-) DCV at DAQ power supply - I changed to Vpurple to wire white = (-) DCV at DAQ power supply and Vred to wire red = common | Vbrown to IAQbrown | Vred to IAQred | Vpurple to IAQwhite at (-) VDC at DAQ power supply | Vblue to IAQgreen at (+) 24VDC at DAQ power supply |  | Vaisala yellow to wire black = temp signal at M4C5
|  | 2 | Vaisala HMP45A | 0-1 VDC | RH_Bed3_M3_C2 | *Eventually replace with HMP155s | Vaisala yellow to wire black = temp signal at M4C6, Vaisala blue to wire green = +24VDC at DAQ power supply, Vaisala brown to wire brown = RH signal at M3C2, Vaisala purple and Vaisala red to wire red = common and wire white = (-) DCV at DAQ power supply - I changed to Vpurple to wire white = (-) DCV at DAQ power supply and Vred to wire red = common | Vbrown to IAQbrown | Vred to IAQred | Vpurple to IAQwhite at (-) VDC at DAQ power supply | Vblue to IAQgreen at (+) 24VDC at DAQ power supply |  | Vaisala yellow to wire black = temp signal at M4C6
|  | 3 | Vaisala HMP155 | 0-10 VDC | RH_Liv_M3_C3 | n/a | [Vaisala HMP155 s/n V1940953 calib 5/11/23] Vaisala white to wire black = temp signal at M4C7); Vaisala green to wire red = common, Vaisala yellow to wire brown = RH signal (M3C0), Vaisala blue to wire green = +24VDC at DAQ power supply, Vaisala red to wire white = (-) DCV at DAQ power supply (Vaisala brown, pink, black, gray taped aside with no connections) | Vyellow to IAQbrown | Vgreen to IAQred | Vred to IAQwhite at (-) VDC at DAQ power supply | Vblue to IAQgreen at (+) 24VDC at DAQ power supply | (Vaisala brown, pink, black, gray taped aside with no connections) | Vaisala white to wire black = temp signal at M4C7)
|  | 4 | Vaisala HMP155 | 0-10 VDC | RH_Fam_M3_C4 | n/a | [Vaisala HMP155 s/n V1940955 calib 5/11/23] Vaisala white to wire black = temp signal at M5C0); Vaisala green to wire red = common, Vaisala yellow to wire brown = RH signal (M3C0), Vaisala blue to wire green = +24VDC at DAQ power supply, Vaisala red to wire white = (-) DCV at DAQ power supply (Vaisala brown, pink, black, gray taped aside with no connections) | Vyellow to IAQbrown | Vgreen to IAQred | Vred to IAQwhite at (-) VDC at DAQ power supply | Vblue to IAQgreen at (+) 24VDC at DAQ power supply | (Vaisala brown, pink, black, gray taped aside with no connections) | Vaisala white to wire black = temp signal at M5C0)
|  | 5 | Vaisala HMP45A | 0-1 VDC | RH_MBa_M3_C5 | *Eventually replace with HMP155s | (Vaisala HMP45A s/n X0630021 calibrated 6/16/23) Vaisala yellow to wire black = temp signal at M5C4, Vaisala blue to wire green = +24VDC at DAQ power supply, Vaisala brown to wire brown = RH signal at M4C0, Vaisala purple and Vaisala red to wire red = common and wire white = (-) DCV at DAQ power supply - I changed to Vpurple to wire white = (-) DCV at DAQ power supply and Vred to wire red = common
|  | 6 | Vaisala HMP45a | 0-1 VDC | RH_Ba1_M3_C6 | *Eventually replace with HMP155s
|  | 7 | Vaisala HMP45a | 0-1 VDC | RH_UR_M3_C7 | *Eventually replace with HMP155s
| 4: NI 9201 AI module | 0 | Vaisala HMP45A | 0-1 VDC | RH_Gar_M4_C0 11/21/25 moved garage Vais to master bath; to this DAQ channel | *Eventually replace with HMP155s | (Vaisala HMP45A s/n X0630021 calibrated 6/16/23) Vaisala yellow to wire black = temp signal at M5C4, Vaisala blue to wire green = +24VDC at DAQ power supply, Vaisala brown to wire brown = RH signal at M4C0, Vaisala purple and Vaisala red to wire red = common and wire white = (-) DCV at DAQ power supply - I changed to Vpurple to wire white = (-) DCV at DAQ power supply and Vred to wire red = common | Vbrown to IAQbrown | Vred to IAQred | Vpurple to IAQwhite at (-) VDC at DAQ power supply | Vblue to IAQgreen at (+) 24VDC at DAQ power supply |  | Vaisala yellow to wire black = temp signal at M5C4
|  | 1 | Vaisala HMP45A | 0-1 VDC | RH_Attic_M4_C1 | *Eventually replace with HMP155s | Vaisala yellow to wire black = temp signal at M5C5, Vaisala blue to wire green = +24VDC at DAQ power supply, Vaisala brown to wire brown = RH signal at M4C1, Vaisala purple and Vaisala red to wire red = common and wire white = (-) DCV at DAQ power supply - I changed to Vpurple to wire white = (-) DCV at DAQ power supply and Vred to wire red = common | Vbrown to IAQbrown | Vred to IAQred | Vpurple to IAQwhite at (-) VDC at DAQ power supply | Vblue to IAQgreen at (+) 24VDC at DAQ power supply |  | Vaisala yellow to wire black = temp signal at M5C5
|  | 2 | Vaisala HMP45A | 0-1 VDC | RH_Out_M4_C2 | *Eventually replace with HMP155s | Vaisala yellow to wire black = temp signal at M5C6, Vaisala blue to wire green = +24VDC at DAQ power supply, Vaisala brown to wire brown = RH signal at M4C2, Vaisala purple and Vaisala red to wire red = common and wire white = (-) DCV at DAQ power supply - I changed to Vpurple to wire white = (-) DCV at DAQ power supply and Vred to wire red = common | Vbrown to IAQbrown | Vred to IAQred | Vpurple to IAQwhite at (-) VDC at DAQ power supply | Vblue to IAQgreen at (+) 24VDC at DAQ power supply |  | Vaisala yellow to wire black = temp signal at M5C6
|  | 3 | Vaisala HMP155 | 0-10 VDC | RH_HVAC-S_M4_C3 | n/a | [Vaisala HMP155 s/n V1940952 calib 5/11/23] Vaisala white to wire black = temp signal at M5C7); Vaisala green to wire red = common, Vaisala yellow to wire brown = RH signal (M3C0), Vaisala blue to wire green = +24VDC at DAQ power supply, Vaisala red to wire white = (-) DCV at DAQ power supply (Vaisala brown, pink, black, gray taped aside with no connections) | Vyellow to IAQbrown | Vgreen to IAQred | Vred to IAQwhite at (-) VDC at DAQ power supply | Vblue to IAQgreen at (+) 24VDC at DAQ power supply | (Vaisala brown, pink, black, gray taped aside with no connections) | Vaisala white to wire black = temp signal at M5C7)
|  | 4 | Vaisala HMP155 | 0-10 VDC | T_Bed1_M4_C4 | *Remove once TCs installed? | see M3C0 above with instrument's RH wiring | Vwhite to IAQblack
|  | 5 | Vaisala HMP45A | 0-1 VDC | T_Bed2_M4_C5 | *Remove once TCs installed? | see M3C1 above with instrument's RH wiring | Vyellow to IAQblack
|  | 6 | Vaisala HMP45A | 0-1 VDC | T_Bed3_M4_C6 | *Remove once TCs installed? | see M3C2 above with instrument's RH wiring | Vyellow to IAQblack
|  | 7 | Vaisala HMP155 | 0-10 VDC | T_Liv_M4_C7 | *Remove once TCs installed? | see M3C3 above with instrument's RH wiring | Vwhite to IAQblack
| 5: NI 9201 AI module | 0 | Vaisala HMP155 | 0-10 VDC | T_Fam_M5_C0 | *Remove once TCs installed? | see M3C4 above with instrument's RH wiring | Vwhite to IAQblack
|  | 1 | Vaisala HMP45A | 0-1 VDC | T_MBa_M5_C1 | *Remove once TCs installed? | see M3C5 above with instrument's RH wiring
|  | 2 | Vaisala HMP45a | 0-1 VDC | T_Ba1_M5_C2 | *Remove once TCs installed?
|  | 3 | Vaisala HMP45a | 0-1 VDC | T_UR_M5_C3 | *Remove once TCs installed?
|  | 4 | Vaisala HMP45A | 0-1 VDC | T_Gar_M5_C4 11/21/25 moved garage Vais to master bath; to this DAQ channel | *Remove once TCs installed? | see M4C0 above with instrument's RH wiring | Vyellow to IAQblack
|  | 5 | Vaisala HMP45A | 0-1 VDC | T_Attic_M5_C5 | *Remove once TCs installed? | see M4C1 above with instrument's RH wiring | Vyellow to IAQblack
|  | 6 | Vaisala HMP45A | 0-1 VDC | T_Out_M5_C6 | *Remove once TCs installed? | see M4C2 above with instrument's RH wiring | Vyellow to IAQblack
|  | 7 | Vaisala HMP155 | 0-10 VDC | T_HVAC-S_M5_C7 | *Remove once TCs installed? | see M4C3 above with instrument's RH wiring | Vwhite to IAQblack
| 6: open ; NI 9481 ? relay module possible future addition | 0 | TSI8455-12 | n/a | AF_HVAC-N_M6_C0 | *Add Relay or anemometer?
|  | 1 | TSI8455-12 | n/a | AF_HVAC-S_M6_C1 | *Add Relay or anemometer?
|  | 2 | (?) | (?) | P_HouseFan_M6_C2 | *Add Relay for HouseFan ON/OFF?
|  | 3 | (?) | (?) | Inj_SF6_M?_C? | *Add SF6 injection relay?
7: open
| 8: open ; NI 9213 ? Possible future addition | 0 | Thermocouple | 0-1 VDC | T_Bed1_M8_C0 | * New TC
|  | 1 | Thermocouple | 0-1 VDC | T_Bed2_M8_C1 | * New TC
|  | 2 | Thermocouple | 0-1 VDC | T_Bed3_M8_C2 | * New TC
|  | 3 | Thermocouple | 0-1 VDC | T_Liv_M8_C3 | * New TC
|  | 4 | Thermocouple | 0-1 VDC | T_Din_M8_C4 | * New TC
|  | 5 | Thermocouple | 0-1 VDC | T_Kit_M8_C5 | * New TC
|  | 6 | Thermocouple | 0-1 VDC | T_Fam_M8_C6 | * New TC
|  | 7 | Thermocouple | 0-1 VDC | T_MBa_M8_C7 | * New TC
|  | 8 | Thermocouple | 0-1 VDC | T_Ba1_M8_C8 | * New TC
|  | 9 | Thermocouple | 0-1 VDC | T_UR_M8_C9 | * New TC
|  | 10 | Thermocouple | 0-1 VDC | T_Gar_M8_C10 | * New TC
|  | 11 | Thermocouple | 0-1 VDC | T_Attic_M8_C11 | * New TC
|  | 12 | Thermocouple | 0-1 VDC | T_Out_M8_C12 | * New TC
|  | 13 | Thermocouple | 0-1 VDC | T_HVAC-S_M8_C13 | * New TC
|  | 14 | Thermocouple | 0-1 VDC | T_Crawl_M8_C14 | * New TC
|  | 15 | n/a | n/a | n/a | n/a